# SUPPLEMENTARY MATERIAL

# Assessing the Environmental Sustainability of Alternative Design Concepts for Transmission Systems of Offshore Renewable Energy

Leonardo Bozzoli1, Mariasole Cipolletta1, Alessandro Dal Pozzo1,

Carlo Alberto Nucci2, Valerio Cozzani1*

1 LISES – Laboratory of Industrial Safety and Environmental Sustainability, Department of Civil, Chemical, Environmental and Materials Engineering (DICAM), University of Bologna, Italy

2 Department of Electrical, Electronic and Information Engineering (DEI), University of Bologna, Italy

*corresponding author: valerio.cozzani@unibo.it

# SM1. Material estimate: offshore substations

Table S-1: Jacket information.

| Jacket |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| HVAC, HVDC, O&G | Structure type | Location | Height | Weight | Topside weight | References |
|  |  |  | m | kg | kg |  |
|  | Gas field | Germany | 60 | 1250000 | 950000 | [1] |
|  | Oil & Gas field | United Kingdom | 47 | 1050000 | 750000 | [2] |
|  | Oil & Gas field | United Kingdom | 55 | 1300000 | 900000 | [3] |
|  | Oil & Gas field | Norway | 170 | 16500000 | 4900000 | [4] |
|  | Wind farm substation | Germany | 51 | 1700000 | 2300000 | [5] |
|  | Wind farm substation | United Kingdom | 30 | 2600000 | 2900000 | [6] |
|  | Wind farm substation | United Kingdom | 42 | 800000 | 1500000 | [7] |
|  | Wind farm substation | Denmark | 50 | 1790000 | 1930000 | [8] |
|  | Gas field | Saudi Arabia | 53 | 2000000 | 5500000 | [9] |
|  | Gas field | Saudi Arabia | 60 | 2100000 | 5500000 | [9] |
|  | Wind farm substation | Germany | 50 | 1800000 | 4000000 | [10] |
|  | Wind Turbine jacket | South Korea | 62 | 1100000 | 800000 | [11] |
|  | Gas & Condensate field | Vietnam | 113 | 12600000 | 14500000 | [12] |
|  | Oil Field | - | 100 | 632000 |  | [13] |
|  | Oil Field | Lufeng | 302 | 30000000 |  | [14] |
|  | Wind Turbine | Aberdeen | 77 | 1800000 |  | [15] |
|  | Wind farm substation | Taiwan | 50 | 3700000 |  | [16] |
|  | Oil field | China | 306 | 40000000 |  | [17] |
|  | Wind farm substation | Germany/ Netherland | 25 | 4500000 | 10300000 | [18] |
|  | Wind farm substation | Germany/ Netherland | 29 | 4000000 | 11000000 | [19] |
|  | Wind farm substation | Germany/ Netherland | 30 | 10000000 | 18000000 | [20] |
|  | Wind farm substation | Germany/ Netherland | 40 | 1800000 | 3200000 | [21] |
|  | Wind farm substation | Germany/ Netherland | 40 | 5600000 | 18000000 | [22] |
|  | Wind farm substation | Germany/ Netherland | 40 | 7500000 | 12000000 | [23] |
|  | Wind farm substation | Germany/ Netherland | 28 | 5600000 | 15000000 | [24] |
|  | Wind farm substation | Germany/ Netherland | 29 | 5250000 | 11300000 | [25] |

Table S-2: Topside information.

| Topside |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Windfarm’s HVAC substations | Structure name | Distance from shore | Power | Voltage | Weight | References |
|  |  | km | MW | kV | kg |  |
|  | Hornsea | 120 | 400 | 220 | 2800000 | [26], [27] |
|  | Nordsee One | 45 | 400 | 155 | 2300000 | [5], [28] |
|  | Arkona | 35 | 385 | 220 | 4000000 | [29] |
|  | Horns Rev | 14 | 160 | 150 | 1100000 | [30] |
|  | Gwynt y Môr | 18 | 288 | 132 | 1300000 | [7] |
|  | Northwind | 37 | 216 | 220 | 1140000 | [31] |
|  | West of Duddon Sands | 14 | 389 | 150 | 1580000 | [31] |
|  | Humber Gateway | 8 | 219 | 132 | 1140000 | [31] |
|  | Westermost Rough | 8 | 210 | 155 | 1500000 | [31] |
|  | Race Bank | 27 | 537 | 220 | 2900000 | [6] |
|  | Borkum Riffgrund | 55 | 320 | n.a. | 1880000 | [31] |
|  | Dan Tysk | 70 | 288 | to HVDC | 3200000 | [31] |
|  | Nordsee Ost | 57 | 295 | n.a. | 1600000 | [31] |
|  | Amrumbank West | 35 | 288 | to HVDC | 2160000 | [31] |
|  | Meerwind | 23 | 288 | n.a. | 3300000 | [31] |
|  | Gode Wind | 40 | 291 | n.a. | 1950000 | [31] |
|  | Dudgeon | 32 | 402 | n.a. | 1800000 | [31] |
| Windfarm’s HVDC substations | Structure name | Distance from shore | Power | Voltage | Weight | References |
|  |  | km | MW | kV | kg |  |
|  | HelWin Alpha | 130 | 576 | 250 | 12000000 | [31], [32] |
|  | HelWin Beta | 130 | 690 | 320 | 10300000 | [18] |
|  | DolWin Alpha | 165 | 800 | 320 | 11000000 | [19] |
|  | DolWin Beta | 135 | 900 | 320 | 15000000 | [31] |
|  | DolWin Gamma | 160 | 900 | 320 | 18000000 | [20] |
|  | DolWin Kappa | 135 | 900 | 320 | 11300000 | [25] |
|  | BorWin Alpha | 200 | 400 | 150 | 3200000 | [21] |
|  | BorWin Beta | 200 | 800 | 300 | 12000000 | [33] |
|  | BorWin Gamma | 230 | 900 | 320 | 18000000 | [22] |
|  | BorWin Epsilon | 230 | 900 | 320 | 12000000 | [23] |
|  | SylWin Alpha | 205 | 864 | 320 | 15000000 | [34] |

Figure S-1:HVDC topsides weight curve from topside function of power and voltage. Fitting obtained from real data interpolation.

Linear model Poly11:

f(x,y) = p00 + p10*x + p01*y

Coefficients (with 95% confidence bounds):

p00 =  -4.196e+06 (-1.534e+07, 6.952e+06)

p10 =   2.055e+04 (-8397, 4.949e+04)

p01 =        3270 (-8.567e+04, 9.221e+04)

Goodness of fit:

SSE: 4.711e+13

R-square: 0.7181

Adjusted R-square: 0.6375

RMSE: 2.594e+06

Figure S-2: jacket weight curve as a function of topside weight and water depth. Fitting obtained from real data interpolation.

Linear model Poly11:

f(x,y) = p00 + p10*x + p01*y

Coefficients (with 95% confidence bounds):

p00 = -4.055e+06 (-5.749e+06, -2.36e+06)

p10 =   9.436e+04 (7.221e+04, 1.165e+05)

p01 =      0.4944 (0.3719, 0.617)

Goodness of fit:

SSE: 4.258e+13

R-square: 0.88

Adjusted R-square: 0.8667

RMSE: 1.538e+06

Figure S-3: HVAC topsides weight curve from topside function of power and voltage. Fitting obtained from real data interpolation.

Linear model Poly11:

f(x,y) = p00 + p10*x + p01*y

Coefficients (with 95% confidence bounds):

p00 = -4.654e+05 (-1.831e+06, 9.003e+05)

p10 =        4483 (1818, 7148)

p01 =        4766 (-3932, 1.346e+04)

Goodness of fit:

SSE: 7.055e+11

R-square: 0.8315

Adjusted R-square: 0.7754

RMSE: 3.429e+05

# SM2. Material estimate: onshore substation

The following data provides an estimation of the weight for onshore HVDC substation.

Concrete proportion: 80 kg/m2 of area occupied by the substation; derived from the number of concrete piles in the Triton Knoll project, multiplied by the assumed volume of each pile times the concrete density.

Gravel proportion: 640 kg/m2 of area occupied by the substation; derived from the amount of gravel used in Triton Knoll project.

Cooler transformer weight is assumed to be 20% of the transformer weight.

Shunt reactor weight is assumed to be 50% of the transformer weight.

Static Var Compensator (SCV) weight is assumed to be 30% of the transformer weight.

Harmonic filter weight is assumed to be 30% of the transformer weight.

The weight of the other minor devices and buildings is assumed to be twice the transformer weight.

Table S-3: data collection and material estimate of onshore HVAC substations. In dark green, values gathered from gray literature, in light green, values assumed or calculated.

| Name of link/substation |  | Triton Knoll | Moray East | Dudgeon | Beatrice |
| --- | --- | --- | --- | --- | --- |
| Gravel | kg | 30000000 | 32000000 | 22400000 | 25600000 |
| Concrete | kg | 3960000 | 4000000 | 2800000 | 3200000 |
| Steel | kg | 2160000 | 3051000 | 1560000 | 1980000 |
| Concrete density | kg/m3 | 2400 | 2400 | 2400 | 2400 |
| volume of each pile | m3 | 1 | 1 | 1 | 1 |
| number of piles | # | 1650 | n.a. | n.a. | n.a. |
| weight of transformer | kg | 240000 | 270000 | 200000 | 198000 |
| number of transformers | # | 2 | 3 | 2 | 2 |
| cooler transformer weight | kg | 48000 | 54000 | 40000 | 39600 |
| number of shunt reactors | # | 2 | 6 | 2 | 4 |
| weight of shunt reactors | kg | 120000 | 135000 | 100000 | 99000 |
| weight of SVC | kg | 72000 | 81000 | 60000 | 59400 |
| number of SVC | # | 12 | 3 | 6 | 6 |
| Number of banks of harmonic filters | # | n.a. | 6 | 2 | 6 |
| Harmonic filter weight | kg | n.a. | 81000 | 60000 | 59400 |
| weight of other equipment | kg | 480000 | 540000 | 400000 | 396000 |
| Area estimation (from Google Maps) | m2 | 47000 | 50000 | 35000 | 40000 |
| Power transmitted | MW | 857 | 950 | 402 | 588 |
| Type |  | HVAC | HVAC | HVAC | HVAC |
| Distance from shore | km | 33 | 30 | 38 | 50 |
| Export cable voltage | kV | 220 | 220 | 132 | 132 |
| Array cable voltage | kV | 33 | 66 | 33 | 33 |
| Connection to grid voltage | kV | 400 | 275 | 400 | 400 |
| Reference/maps view |  | [35] | [36] | [37] | [38] |

Table S-4: weight normalization on power basis for main composing materials of onshore substation and average value.

|  |  | Triton Knoll | Moray East | Dudgeon | Beatrice | Average values |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Normalized values |  |  |  |  |
| Gravel | kg/MW | 35006 | 33684 | 55721 | 43537 | 41987 |
| Concrete | kg/MW | 4621 | 4211 | 6965 | 5442 | 5309 |
| Steel | kg/MW | 2520 | 3212 | 3881 | 3367 | 3244 |

The average values reported in Table S-4 are used to calculate the weight of materials used in building the onshore substation.

The following data provides an estimation of the weight for onshore HVDC substation.

Here, the same proportions considered for the HVAC onshore substation amount estimation of gravel and cement is used, 80 kg/m2 and 640 kg/m2 of area occupied by the substation for cement and gravel respectively.

From [39] data regarding weights of switchgears and reactors are gathered while from [40] weights regarding reactor are collected.

Converter weight is assumed to be 10% of the converter transformer weight.

The weight of other equipment is assumed to be twice the weight of the converter transformer.

50 kg/m2 of area occupied by the valve hall are used to estimate the steel in the building structure, as reported in [41].

The amount of steel and stainless steel is assumed to be 50 % of the total final amount reported in Table S-4.

Table S-5: data collection and material estimate of onshore HVDC substations. In dark green, values gathered from gray literature, in light green, values assumed or calculated.

|  |  | COBRA cable (Emshaven station) | COBRA cable (Endrup station) | Dörpen West substation | Caithness - Moray Link |
| --- | --- | --- | --- | --- | --- |
| Gravel | kg | 17920000 | 23040000 | 32000000 | 42880000 |
| Concrete | kg | 2912000 | 3744000 | 5200000 | 6968000 |
| Steel | kg | 2325000 | 2325000 | 2385000 | 2874000 |
| Converter transformer | kg | 400000 | 400000 | 500000 | 500000 |
| Number of transformers | # | 3 | 3 | 2 | 3 |
| AC/DC Converter | kg | 40000 | 40000 | 50000 | 49000 |
| Valve hall kg of steel | kg | 185000 | 185000 | 235000 | 275000 |
| Valve hall dimension - Dolwin 2 | m2 | 3700 | 3700 | 4700 | 5500 |
| DC smoothing reactor weight | kg | 14000 | 14000 | 14000 | 14000 |
| DC smoothing reactor number | # | 4 | 4 | 4 | 4 |
| DC harmonic filter weight | kg | 14000 | 14000 | 14000 | 14000 |
| DC harmonic filter number | # | 2 | 2 | 2 | 2 |
| DC switchyard | kg | 16000 | 16000 | 16000 | 16000 |
| Weight of other equipment | kg | 800000 | 800000 | 1000000 | 980000 |
| Area estimation (from Google Maps) | m2 | 28000 | 36000 | 50000 | 67000 |
| Power | MW | 700 | 700 | 900 | 1200 |
| Voltage | kV | 320 | 320 | 320 | 320 |
| Reference/maps view |  | [42] | [43] | [44], [45] | [46] |

Table S-6: weight normalization on power basis for main composing materials of onshore substation and average value.

|  |  | COBRA cable (Emshaven station) | COBRA cable (endrup station) | Dolwin 3 | scottish link | Average values |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Normalized values |  |  |  |  |
| Gravel | kg/MW | 25600 | 32914 | 35555 | 35733 | 32450 |
| Concrete | kg/MW | 4160 | 5348 | 5777 | 5806 | 5273 |
| Steel | kg/MW | 3321 | 3321 | 2650 | 2395 | 2921 |

The average values reported in Table S-6 are used to calculate the weight of materials used in building the onshore substation

# SM3. Material estimate: export cable

In this section, Figures S-4 and S-5 show the stratigraphies adopted to modelling the weights of the cables, while in Tables from S-7 and S-26 are reported the thickness and technical characteristics of the considered cables.

Figure S-4: single-core cable stratigraphy. XLPE: cross linked polyethylene; PP: polypropylene.

Table S-7:single-core HVAC (220 kV - 1400 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [47] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 220 | kV | Cost | supply | lay |
|  |  | Ampacity | 1450 | A |  | 2400 | 450 |
|  |  | cross section | 1400 | mm2 |  |  |  |
|  |  | Resistance [48] | 0.037 | Ω/m | Cumulated radius | volume (cm3/m) | % |
|  |  | Inductance | 1.32 | mH/km |  |  |  |
| Copper wire |  | Conductor | 44.4 | mm | 22.2 | 1548 | 12.38 |
| HDPE |  | Conductor Binder | 0.7 | mm | 22.9 | 99 | 0.79 |
| XLPE +Carbon |  | Conductor shield | 1 | mm | 23.9 | 147 | 1.18 |
| XLPE |  | Insulation | 23 | mm | 46.9 | 5116 | 40.90 |
|  |  | Diameter over the insulation | 93.8 | mm | 93.8 |  |  |
| XLPE +Carbon |  | Insulation shield | 1 | mm | 47.9 | 298 | 2.38 |
|  |  | Longitudinal water barrier | 0.6 | mm | 48.5 | 182 | 1.45 |
| lead |  | Metallic sheath | 3.1 | mm | 51.6 | 975 | 7.79 |
| HDPE |  | Inner sheath | 2.5 | mm | 54.1 | 830 | 6.64 |
| galv. Steel |  | Armour | 5 | mm | 59.1 | 1778 | 14.22 |
| PP |  | Outer serving | 4 | mm | 63.1 | 1536 | 12.28 |
|  |  | Total diameter | 126.2 | mm |  | 12509 | 100.00 |
|  |  | Total diameter | 128.6 | mm | PN [MW] | 552 |  |

Table S-8:single-core HVAC (220 kV - 1400 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 12.4 | 44.5 | 7.8 | 7.4 | 14.2 | 12.3 |
| total V [cm3/m] | 1548 | 5561 | 975 | 929 | 1778 | 1536 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 13.9 | 5.2 | 11.0 | 0.9 | 14.0 | 1.4 |
| total Mass % | 29.9 | 11.2 | 23.8 | 1.9 | 30.3 | 3.0 |

Table S-9:single-core HVAC (220 kV - 1600 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [47] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 220 | kV | Cost | supply | lay |
|  |  | Ampacity | 1680 | A |  | 2550 | 450 |
|  |  | cross section | 1600 | mm2 |  |  |  |
|  |  | Resistance [48] | 0.036 | Ω/m | Cumulated radius | volume (cm3/m) | % |
|  |  | Inductance | 1.31 | mH/km |  |  |  |
| Copper wire |  | Conductor | 47.4 | mm | 23.7 | 1765 | 13.46 |
| HDPE |  | Conductor Binder | 0.7 | mm | 24.4 | 106 | 0.81 |
| XLPE +Carbon |  | Conductor shield | 1 | mm | 25.4 | 156 | 1.19 |
| XLPE |  | Insulation | 23 | mm | 48.4 | 5333 | 40.67 |
|  |  | Diameter over the insulation | 96.8 | mm | 96.8 |  |  |
| XLPE +Carbon |  | Insulation shield | 1 | mm | 49.4 | 307 | 2.34 |
|  |  | Longitudinal water barrier | 0.6 | mm | 50 | 187 | 1.43 |
| lead |  | Metallic sheath | 3.1 | mm | 53.1 | 1004 | 7.66 |
| HDPE |  | Inner sheath | 2.5 | mm | 55.6 | 854 | 6.51 |
| galv. Steel |  | Armour | 5 | mm | 60.6 | 1825 | 13.92 |
| PP |  | Outer serving | 4 | mm | 64.6 | 1573 | 12.00 |
|  |  | Total diameter | 129.2 | mm |  | 13110 | 100.00 |
|  |  | Total diameter | 131.8 | mm | PN [MW] | 640 |  |

Table S-10:single-core HVAC (220 kV - 1600 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 13.5 | 44.2 | 7.7 | 7.3 | 13.9 | 12.0 |
| total V [cm3/m] | 1765 | 5796 | 1004 | 960 | 1825 | 1573 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 15.8 | 5.4 | 11.3 | 0.9 | 14.4 | 1.4 |
| total Mass % | 32.1 | 10.9 | 23.0 | 1.8 | 29.3 | 2.9 |

Table S-11:single-core HVAC (400 kV - 1400 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [47] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 400 | kV | Cost | supply | lay |
|  |  | Ampacity | 1450 | A |  | 2500 | 450 |
|  |  | cross section | 1400 | mm2 |  |  |  |
|  |  | Resistance [48] | 0.035 | Ω/m | Cumulated radius | volume (cm3/m) | % |
|  |  | Inductance | 1.32 | mH/km |  |  |  |
| Copper wire |  | Conductor | 44.4 | mm | 22.2 | 1548 | 10.78 |
| HDPE |  | Conductor Binder | 0.8 | mm | 23 | 114 | 0.79 |
| XLPE +Carbon |  | Conductor shield | 1.4 | mm | 24.4 | 208 | 1.45 |
| XLPE |  | Insulation | 27 | mm | 51.4 | 6430 | 44.79 |
|  |  | Diameter over the insulation | 102.8 | mm | 102.8 |  |  |
| XLPE +Carbon |  | Insulation shield | 1 | mm | 52.4 | 326 | 2.27 |
|  |  | Longitudinal water barrier | 0.6 | mm | 53 | 199 | 1.38 |
| lead |  | Metallic sheath | 3.1 | mm | 56.1 | 1063 | 7.40 |
| HDPE |  | Inner sheath | 2.5 | mm | 58.6 | 901 | 6.27 |
| galv. Steel |  | Armour | 5 | mm | 63.6 | 1920 | 13.37 |
| PP |  | Outer serving | 4 | mm | 67.6 | 1649 | 11.48 |
|  |  | Total diameter | 135.2 | mm |  | 14356 | 100.00 |
|  |  | Total diameter | 138 | mm | PN [MW] | 1004 |  |

Table S-12:single-core HVAC (400 kV - 1400 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 10.8 | 48.5 | 7.4 | 7.1 | 13.4 | 11.5 |
| total V [cm3/m] | 1548 | 6964 | 1063 | 1014 | 1920 | 1649 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 13.9 | 6.5 | 12.0 | 1.0 | 15.2 | 1.5 |
| total Mass % | 27.8 | 13.0 | 24.0 | 1.9 | 30.3 | 3.0 |

Table S-13:single-core HVAC (400 kV - 1600 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [47] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 400 | kV | Cost | supply | lay |
|  |  | Ampacity | 1680 | A |  | 2750 | 450 |
|  |  | cross section | 1600 | mm2 |  |  |  |
|  |  | Resistance [48] | 0.033 | Ω/m | Cumulated radius | volume (cm3/m) | % |
|  |  | Inductance | 1.31 | mH/km |  |  |  |
| Copper wire |  | Conductor | 47.4 | mm | 23.7 | 1765 | 11.76 |
| HDPE |  | Conductor Binder | 0.8 | mm | 24.5 | 121 | 0.81 |
| XLPE +Carbon |  | Conductor shield | 1.4 | mm | 25.9 | 222 | 1.48 |
| XLPE |  | Insulation | 27 | mm | 52.9 | 6684 | 44.56 |
|  |  | Diameter over the insulation | 105.8 | mm | 105.8 |  |  |
| XLPE +Carbon |  | Insulation shield | 1 | mm | 53.9 | 336 | 2.24 |
|  |  | Longitudinal water barrier | 0.6 | mm | 54.5 | 204 | 1.36 |
| lead |  | Metallic sheath | 3.1 | mm | 57.6 | 1092 | 7.28 |
| HDPE |  | Inner sheath | 2.5 | mm | 60.1 | 924 | 6.16 |
| galv. Steel |  | Armour | 5 | mm | 65.1 | 1967 | 13.11 |
| PP |  | Outer serving | 4 | mm | 69.1 | 1686 | 11.24 |
|  |  | Total diameter | 138.2 | mm |  | 15001 | 100.00 |
|  |  | Total diameter | 141 | mm | PN [MW] | 1163 |  |

Table S-14:single-core HVAC (400 kV - 1600 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 11.8 | 48.3 | 7.3 | 7.0 | 13.1 | 11.2 |
| total V [cm3/m] | 1765 | 7241 | 1092 | 1046 | 1967 | 1686 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 15.8 | 6.7 | 12.3 | 1.0 | 15.5 | 1.5 |
| total Mass % | 29.9 | 12.7 | 23.3 | 1.9 | 29.4 | 2.9 |

Table S-15:single-core HVDC (150 kV - 500 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [47] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage |  | 150 | kV | Cost | supply | lay |
|  |  | Ampacity |  | 883 | A |  | 600 | 450 |
|  |  | cross section |  | 500 | mm2 |  |  |  |
|  |  | Resistance [49] |  | 0.044 | Ω/m | Cumulated radius | volume (cm3/m) | % |
| Copper wire |  |  | Conductor | 26.2 | mm | 13.1 | 539 | 7.74 |
| HDPE |  |  | Conductor Binder | 1.2 | mm | 14.3 | 103 | 1.48 |
| XLPE +Carbon |  |  | Conductor shield | 2 | mm | 16.3 | 192 | 2.76 |
| XLPE |  |  | Insulation | 17 | mm | 33.3 | 2649 | 38.01 |
| XLPE +Carbon |  |  | Insulation shield | 0 | mm | 33.3 | 0 | 0.00 |
|  |  |  | Longitudinal water barrier | 0.8 | mm | 34.1 | 169 | 2.43 |
| lead |  |  | Metallic sheath | 2.5 | mm | 36.6 | 555 | 7.97 |
| HDPE |  |  | Inner sheath | 1.5 | mm | 38.1 | 352 | 5.05 |
| galv. Steel |  |  | Armour [50] | 5 | mm | 43.1 | 1275 | 18.30 |
| PP |  |  | Outer serving | 4 | mm | 47.1 | 1133 | 16.26 |
|  |  | Total diameter |  | 94.2 | mm |  | 6969 | 100.00 |
|  |  | Total diameter |  | 102.2 | mm | PN [MW] | 264 |  |

Table S-16:single-core HVDC (150 kV - 500 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 7.7 | 40.8 | 8.0 | 6.5 | 18.3 | 16.3 |
| total V [cm3/m] | 539 | 2841 | 555 | 455 | 1275 | 1133 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 4.8 | 2.6 | 6.3 | 0.4 | 10.1 | 1.0 |
| total Mass % | 19.1 | 10.5 | 24.8 | 1.7 | 39.9 | 4.0 |

Table S-17:single-core HVDC (320 kV - 630 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [51] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 320 | kV | Cost | supply | lay |
|  |  | Ampacity | 1023 | A |  | 740 | 450 |
|  |  | cross section | 630 | mm2 |  |  |  |
|  |  | Resistance [49] | 0.034 | Ω/m | Cumulated radius | volume (cm3/m) | % |
| Copper wire |  | Conductor | 29.8 | mm | 14.9 | 697 | 7.79 |
| HDPE |  | Conductor Binder | 0.6 | mm | 15.5 | 57 | 0.64 |
| XLPE +Carbon |  | Conductor shield | 1.5 | mm | 17 | 153 | 1.71 |
| XLPE |  | Insulation | 20 | mm | 37 | 3393 | 37.87 |
| XLPE +Carbon |  | Insulation shield | 1.4 | mm | 38.4 | 332 | 3.70 |
|  |  | Longitudinal water barrier | 0.6 | mm | 39 | 146 | 1.63 |
| lead |  | Metallic sheath | 2.9 | mm | 41.9 | 737 | 8.23 |
| HDPE |  | Inner sheath | 2.5 | mm | 44.4 | 678 | 7.57 |
| galv. Steel |  | Armour | 5 | mm | 49.4 | 1473 | 16.45 |
| PP |  | Outer serving | 4 | mm | 53.4 | 1292 | 14.42 |
|  |  | Total diameter | 106.8 | mm |  | 8958 | 100.00 |
|  |  | Total diameter | 135 | mm | PN [MW] | 654 |  |

Table S-18:single-core HVDC (320 kV - 630 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 7.8 | 43.3 | 8.2 | 8.2 | 16.4 | 14.4 |
| total V [cm3/m] | 697 | 3878 | 737 | 735 | 1473 | 1292 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 6.2 | 3.6 | 8.3 | 0.7 | 11.6 | 1.2 |
| total Mass % | 19.7 | 11.4 | 26.3 | 2.2 | 36.7 | 3.7 |

Table S-19:single-core HVDC (320 kV - 1400 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  | Submarine Single core Cable Design Sheet [51] |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Voltage | 320 | kV | Cost | supply | lay |
|  |  | Ampacity | 1594 | A |  | 1400 | 450 |
|  |  | cross section | 1400 | mm2 |  |  |  |
|  |  | Resistance [49] | 0.015 | Ω/m | Cumulated radius | volume (cm3/m) | % |
| Copper wire |  | Conductor | 44.4 | mm | 22.2 | 1548 | 13.38 |
| HDPE |  | Conductor Binder | 0.6 | mm | 22.8 | 85 | 0.73 |
| XLPE +Carbon |  | Conductor shield | 1.5 | mm | 24.3 | 222 | 1.92 |
| XLPE |  | Insulation | 20 | mm | 44.3 | 4310 | 37.24 |
| XLPE +Carbon |  | Insulation shield | 1.4 | mm | 45.7 | 396 | 3.42 |
|  |  | Longitudinal water barrier | 0.6 | mm | 46.3 | 173 | 1.50 |
| lead |  | Metallic sheath | 2.9 | mm | 49.2 | 870 | 7.52 |
| HDPE |  | Inner sheath | 2.5 | mm | 51.7 | 792 | 6.85 |
| galv. Steel |  | Armour | 5 | mm | 56.7 | 1703 | 14.71 |
| PP |  | Outer serving | 4 | mm | 60.7 | 1475 | 12.75 |
|  |  | Total diameter | 121.4 | mm |  | 11575 | 100.00 |
|  |  | Total diameter | 135 | mm | PN [MW] | 1020 |  |  |

Table S-20:single-core HVDC (320 kV - 1400 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 13.4 | 42.6 | 7.5 | 7.6 | 14.7 | 12.7 |
| total V [cm3/m] | 1548 | 4928 | 870 | 877 | 1703 | 1475 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 13.9 | 4.6 | 9.8 | 0.8 | 13.5 | 1.3 |
| total Mass % | 31.6 | 10.4 | 22.4 | 1.9 | 30.6 | 3.0 |

Figure S-5: three-core cable stratigraphy.

Table S-21: three-core HVAC (132 kV - 500 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  |  | Submarine three core Cable Design Sheet [47] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Voltage | 132 | kV | Cost | supply | laying |  |
|  |  |  | Ampacity | 720 | A |  | 335 | 300 |  |
|  |  |  | Cross section | 500 | mm2 | Cumulated radius | volume single core (cm3/m) | volume three core (cm3/m) |  |
|  |  |  | Resistance [49] | 0.049 | Ω/km |  |  |  |  |
|  |  |  | Inductance | 0.38 | mH/km |  |  |  | % |
| Copper wire |  | single core | Conductor | 26.2 | mm | 13.1 | 539 | 1617 | 6.6 |
| HDPE |  |  | Conductor Binder | 0.5 | mm | 13.6 | 42 | 126 | 0.5 |
| XLPE +Carbon |  |  | Conductor shield (semi-conducting extruded) | 0.9 | mm | 14.5 | 79 | 238 | 1.0 |
| XLPE |  |  | Insulation | 15 | mm | 29.5 | 2073 | 6220 | 25.6 |
|  |  |  | Diameter over the insulation | 59 | mm | 59 |  |  |  |
| XLPE +Carbon |  |  | Insulation shield (semi-conducting extruded) | 1.4 | mm | 30.9 | 266 | 797 | 3.3 |
|  |  |  | Longitudinal water barrier | 0.6 | mm | 31.5 | 118 | 353 | 1.5 |
| lead |  |  | Metallic sheath | 2.3 | mm | 33.8 | 472 | 1416 | 5.8 |
|  |  |  | single core diameter | 67.6 |  |  | 3589 | 10767 |  |
| PP |  | PP filler | PE/PP filler |  |  |  | 8346 |  | 34.3 |
|  |  |  | three core inside radius | 78 |  |  | 19113 |  |  |
| HDPE |  | Outer sheath | Inner sheath | 2.5 | mm | 80.5 | 1245 |  | 5.1 |
| galv. Steel |  |  | Armour | 5 | mm | 83 | 1284 |  | 5.3 |
| PP |  |  | Outer serving | 4 | mm | 88 | 2686 |  | 11.0 |
|  |  |  | Total diameter | 176 |  |  | 24328 |  | 100.0 |
|  |  |  | PN [MW] | 164 |  |  |  |  |  |

Table S-22:three-core HVAC (132 kV - 500 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 6.6 | 29.8 | 5.8 | 5.6 | 5.3 | 45.3 |
| total V [cm3/m] | 1617 | 7256 | 1416 | 1371 | 1284 | 11032 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 14.5 | 6.7 | 16.0 | 1.3 | 10.1 | 9.9 |
| total Mass % | 24.7 | 11.5 | 27.3 | 2.2 | 17.3 | 16.9 |

Table S-23: three-core HVAC (220 kV - 500 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  |  | Submarine three core Cable Design Sheet [47] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Voltage | 220 | kV | Cost | supply | laying |  |
|  |  |  | Ampacity | 720 | A |  | 520 | 300 |  |
|  |  |  | cross section | 500 | mm2 |  |  |  |  |
|  |  |  | Resistance | 0.049 | Ω/km | Cumulated radius | volume (cm3/m) | % |  |
|  |  |  | Inductance | 0.43 | mH/km |  |  |  |  |
| Copper wire |  | single core | Conductor | 26.2 | mm | 13.1 | 539 | 1617 | 4.3 |
| HDPE |  |  | Conductor Binder | 0.6 | mm | 13.7 | 51 | 152 | 0.4 |
| XLPE +Carbon |  |  | Conductor shield (semi-conducting extruded) | 1.1 | mm | 14.8 | 98 | 295 | 0.8 |
| XLPE |  |  | Insulation | 24 | mm | 38.8 | 4041 | 12124 | 32.2 |
|  |  |  | Diameter over the insulation | 77.6 | mm | 77.6 |  |  |  |
| XLPE +Carbon |  |  | Insulation shield (semi-conducting extruded) | 1.4 | mm | 40.2 | 347 | 1042 | 2.8 |
|  |  |  | Longitudinal water barrier | 0.6 | mm | 40.8 | 153 | 458 | 1.2 |
| lead |  |  | Metallic sheath | 2.9 | mm | 43.7 | 770 | 2310 | 6.1 |
|  |  |  | single core diameter | 87.4 |  |  | 5999 | 17998 |  |
| PP |  | PP filler | PE / PP filler |  |  |  | 13104 |  | 34.8 |
|  |  |  | three core inside radius | 99.5 |  |  | 31103 |  |  |
| HDPE |  | Outer sheath | Inner sheath | 2.5 | mm | 102 | 1583 |  | 4.2 |
| galv. Steel |  |  | Armour | 5 | mm | 104.5 | 1622 |  | 4.3 |
| PP |  |  | Outer serving | 4 | mm | 109.5 | 3362 |  | 8.9 |
|  |  |  | Total diameter | 219 |  |  | 37668 |  | 100.0 |
|  |  |  | PN [MW] | 274 |  |  |  |  |  |

Table S-24:three-core HVAC (220 kV - 500 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 4.3 | 35.7 | 6.1 | 4.6 | 4.3 | 43.7 |
| total V [cm3/m] | 1617 | 13462 | 2310 | 1734 | 1622 | 16466 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 14.5 | 12.5 | 26.1 | 1.6 | 12.8 | 14.8 |
| total Mass % | 17.6 | 15.2 | 31.7 | 2.0 | 15.6 | 18.0 |

Table S-25: three-core HVAC (220 kV - 630 mm2) submarine power cable stratigraphy and information. Light green thickness values are from the reference data sheet, other thickness values are assumed to fit the given total diameter. XLPE: cross linked polyethylene; HDPE: high density polyethylene; PP: polypropylene; galv. steel: galvanized steel.

|  |  |  | Submarine three core Cable Design Sheet [47] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Voltage | 220 | kV | Cost | supply | laying |  |
|  |  |  | Ampacity | 786 | A |  | 580 | 300 |  |
|  |  |  | cross section | 630 | mm2 |  |  |  |  |
|  |  |  | Resistance | 0.039 | Ω/km | Cumulated radius | volume (cm3/m) | % |  |
|  |  |  | Inductance | 0.41 | mH/km |  |  |  |  |
| Copper wire |  | single core | Conductor | 29.8 | mm | 14.9 | 697 | 2092 | 5.3 |
| HDPE |  |  | Conductor Binder | 0.6 | mm | 15.5 | 57 | 172 | 0.4 |
| XLPE +Carbon |  |  | Conductor shield (semi-conducting extruded) | 1.1 | mm | 16.6 | 111 | 333 | 0.8 |
| XLPE |  |  | Insulation | 23 | mm | 39.6 | 4061 | 12182 | 30.9 |
|  |  |  | Diameter over the insulation | 79.2 | mm | 79.2 |  |  |  |
| XLPE +Carbon |  |  | Insulation shield (semi-conducting extruded) | 1.4 | mm | 41 | 354 | 1063 | 2.7 |
|  |  |  | Longitudinal water barrier | 0.6 | mm | 41.6 | 156 | 467 | 1.2 |
| lead |  |  | Metallic sheath | 3 | mm | 44.6 | 812 | 2437 | 6.2 |
|  |  |  | single core diameter | 89.2 |  |  | 6249 | 18747 |  |
| PP |  | PE filler | PE / PP filler |  |  |  | 13938 |  | 35.4 |
|  |  |  | three core inside radius | 102 |  |  | 32685 |  |  |
| HDPE |  | Outer sheath | Inner sheath | 2.5 | mm | 104.5 | 1622 |  | 4.1 |
| galv. Steel |  |  | Armour | 5 | mm | 107 | 1661 |  | 4.2 |
| PP |  |  | Outer serving | 4 | mm | 112 | 3440 |  | 8.7 |
|  |  |  | Total diameter | 224 |  |  | 39408 |  | 100.0 |
|  |  |  | PN [MW] | 299 |  |  |  |  |  |

Table S-26:three-core HVAC (220 kV - 630 mm2) submarine power cable absolute and percentage volume and mass values.

|  | Copper | XLPE | Lead | HDPE | Galv. Steel | PP |
| --- | --- | --- | --- | --- | --- | --- |
| total %V | 5.3 | 34.5 | 6.2 | 4.6 | 4.2 | 44.1 |
| total V [cm3/m] | 2092 | 13579 | 2437 | 1794 | 1661 | 17378 |
| Density [g/cm3] | 9.0 | 0.9 | 11.3 | 1.0 | 7.9 | 0.9 |
| total Mass [kg/m] | 18.7 | 12.6 | 27.5 | 1.7 | 13.1 | 15.6 |
| total Mass % | 21.0 | 14.1 | 30.8 | 1.9 | 14.7 | 17.5 |

# SM4. Inventory data for the background processes

Data collected from well-known life cycle inventory databases were used to model the background processes, as reported in Table S-27, alongside the reference year and location of the listed datasets. Geographical and time coverage of the datasets are in line with the definition of the system in section 2.1.1 of the main text.

Table S-27: Datasets used in LCI modelling.

| Process | Corresponding dataset adopted in LCI modelling | Source | Year | Location | Link |
| --- | --- | --- | --- | --- | --- |
| Production of copper | Copper mix (99,999% from electrolysis); from electrolysis; consumption mix, to consumer; 99,999% Cu | Thinkstep - Free Gabi data | 2013 | GLO | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=301d375b-4f27-43f2-bbe0-89f87cae0df1&version=09.00.000&stock=Free_GaBi_data |
| Production of steel | Steel cold rolled coil; BF route; production mix, at plant; 1,5 mm | Thinkstep - Free Gabi data | 2013 | DE | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=cfb5da9c-9610-4651-a54b-d89dbf88ca66&version=09.00.000&stock=Free_GaBi_data |
| Production of stainless steel | Stainless Steel slab (X6CrNi17); EAF route; production mix, at plant; X6CrNi17 | Thinkstep - Free Gabi data | 2013 | DE | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=db14c527-8ab6-4f5c-b21c-d5c789e94d82&version=09.00.000&stock=Free_GaBi_data |
| Production of HDPE | High density polyethylene (HDPE), fossil fuel-based; polymerisation of fossil-based ethylene; production mix, at plant; petrochemical based | Ecoinvent - EF3_1_Plastic_public | 2016 | GLO,DE | https://ecoinvent.lca-data.com/showProcess.xhtml?uuid=3a98e254-7d0b-5a85-92bc-03cd916705ec&version=01.01.000&stock=EF3_1_Plastics_public |
| Production of PP | Polypropylene (PP), blend of bio-based and fossil; polymerisation of mix bio-based and fossil-based propylene; production mix, at plant; blend of bio-based and fossil | Ecoinvent - EF3_1_Plastic_public | 2016 | GLO,DE | https://ecoinvent.lca-data.com/showProcess.xhtml?uuid=f78f09a8-1e3b-5191-890d-90b95a8ce0d2&version=01.01.000&stock=EF3_1_Plastics_public |
| Production of lead | Primary lead production from concentrate | Ecoinvent - V3.9 (2022) | 2005 | RER | https://db.ecoinvent.org/processdetail.php?area=2&pid=1103&displaymode=LCI |
| Production of concrete | Ready-mix concrete C12/15; technology mix; production mix, at plant; C12/15 | Thinkstep -Free Gabi data | 2013 | DE | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=c6c0088c-b59b-402a-ba4c-59cc2b46aca2&version=09.00.000&stock=Free_GaBi_data |
| Production of gravel | Gravel 2/32, production mix, at plant, wet and dry quarry, undried | ELCD - 898618b2-3306-11dd-bd11-0800200c9a66 | 2005 | RER | https://eplca.jrc.ec.europa.eu/ELCD3/datasetDownload.xhtml |
| Transportation by truck | Lorry transport, Euro 0, 1, 2, 3, 4 mix, 22 t total weight, 17,3t max payload | ELCD - 50462b0d-7d2b-40d4-843e-9857061e3c08 | 2005 | RER | https://eplca.jrc.ec.europa.eu/ELCD3/datasetDownload.xhtml |
| Production of heavy fuel oil | Heavy fuel oil, consumption mix, at refinery, from crude oil | ELCD - 50462b0d-7d2b-40d4-843e-9857061e3c0 | 2005 | RER | https://eplca.jrc.ec.europa.eu/ELCD3/datasetDownload.xhtml |
| Use of HFO in vessels | Transport, ocean freighter, residual fuel oil powered | National Renewable Energy Laboratory (NREL) USLCI | 2000 | USA | https://www.lcacommons.gov/lca-collaboration/Federal_Highway_Administration/mtu_pavement/dataset/PROCESS/f85fcdde-6c6b-3bbb-8efc-de6cb34c9ac7 |
| Electricity from wind power | Electricity from wind power; AC, technology mix of onshore and offshore; production mix, at plant; 1kV - 60kV | Thinkstep -Free Gabi data | 2011 | EU-27 | https://lcdn.thinkstep.com/datasetdetail/process.xhtml?uuid=fe1c3d03-072b-4da7-8fff-3505f9b01efc&version=09.00.000&stock=Free_GaBi_data |

# SM5. Vessels for installation and maintenance duties

Vessels for the installation and maintenance of cables and offshore substations were assumed to be fuelled by heavy fuel oil (HFO). Emissions from the engine combustion of HFO were estimated according to stoichiometry and literature references [52] . Technical data used for the calculations are detailed in Table S-28.

Table S-28: Ships data

| Operation | Phase | N° of vessels | Speed | Transport capacity | Dynamic positioning operations | Time for installation | Maintenance activities | Ref. |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | # | km/h | tons/day | tons/day | h | #/year |  |
| Cable laying (Giulio Verne ship) | Install. | 1 | 0.25 | 15 - 20 | 10 | - | - | [53] |
| Tugboats for transport of jacket | Install. | 2 | 7.00 | 7 | - | - | - | [54] [55] |
| Tugboats for transport of topside | Install. | 2 | 7.00 | 7 | - | - | - | [54] [55] |
| Vessel, inspection of cables | O&M | 1 | 2.92 | 2 | - | - | 1 | [54] [55] [56] |
| Vessel for maintenance of substation | O&M | 1 | 14.82 | 2 | - | - | 12 | [55] [56] |
| Jack up vessel for substation major replacement | O&M | 1 | 14.82 | 32 | 8 | - | 0.04 | [57] [55] [56] |
| Jack up vessel for installation | O&M | 1 | 14.82 | 44 | 14 | 8 | - | [57] [55] |

# SM6. Supplementary results: baseline scenario

Table S-29: Overall LCIA results for the baseline scenario. HVAC configuration.

| HVAC |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| according to CML2002 | ADm | ADf | CC | HT | FAET | MAET | FSET | MSET | TET | POF | EUT | ACD |
|  | kg.eq Sb/MWh | MJ/MWh | kg.eq CO2/MWh | kg.eq 1,4-DCB/MWh | kg.eq 1,4-DCB/MWh | kg.eq 1,4-DCB/MWh | kg.eq 1,4-DCB/MWh | kg.eq 1,4-DCB/MWh | kg.eq 1,4-DCB/MWh | kg.eq etilene/MWh | kg.eq PO4--/MWh | kg.eq SO2/MWh |
| Whole system | 2.9E-04 | 1.6E+01 | 1.1E+00 | 2.3E-01 | 1.0E+00 | 5.6E+02 | 2.5E+00 | 4.9E+02 | 3.5E-04 | 4.1E-04 | 1.9E-03 | 1.1E-02 |
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |
| Cables | 2.5E-04 | 8.9E+00 | 4.7E-01 | 2.3E-01 | 1.0E+00 | 5.6E+02 | 2.5E+00 | 4.9E+02 | 1.5E-04 | 1.9E-04 | 1.4E-03 | 7.3E-03 |
|  | 87% | 56% | 41% | 98% | 100% | 100% | 100% | 100% | 44% | 46% | 77% | 69% |
| Production | 2.5E-04 | 8.6E+00 | 4.4E-01 | 2.2E-01 | 1.0E+00 | 5.6E+02 | 2.5E+00 | 4.9E+02 | 1.5E-04 | 1.7E-04 | 1.4E-03 | 6.7E-03 |
|  | 87% | 54% | 39% | 98% | 100% | 100% | 100% | 100% | 44% | 41% | 72% | 64% |
| Transports | 6.2E-11 | 3.3E-01 | 2.9E-02 | 7.7E-04 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 2.0E-05 | 8.3E-05 | 5.1E-04 |
|  | 0% | 2% | 3% | 0% | 0% | 0% | 0% | 0% | 0% | 5% | 4% | 5% |
| Offshore substation | 1.1E-05 | 3.6E+00 | 3.8E-01 | 2.5E-03 | 9.6E-05 | 6.5E-02 | 2.4E-04 | 6.4E-02 | 3.8E-05 | 1.7E-04 | 3.2E-04 | 2.1E-03 |
|  | 4% | 23% | 34% | 1% | 0% | 0% | 0% | 0% | 11% | 41% | 17% | 20% |
| Manufacturing | 1.1E-05 | 3.0E+00 | 3.3E-01 | 9.1E-04 | 9.6E-05 | 6.5E-02 | 2.4E-04 | 6.4E-02 | 3.8E-05 | 1.3E-04 | 1.6E-04 | 1.1E-03 |
|  | 4% | 19% | 29% | 0% | 0% | 0% | 0% | 0% | 11% | 31% | 8% | 10% |
| Transports | 1.1E-10 | 5.9E-01 | 5.4E-02 | 1.6E-03 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 4.1E-05 | 1.7E-04 | 1.0E-03 |
|  | 0% | 4% | 5% | 1% | 0% | 0% | 0% | 0% | 0% | 10% | 9% | 10% |
| Onshore substation | 2.3E-05 | 1.1E+00 | 1.1E-01 | 6.1E-04 | 2.0E-04 | 1.4E-01 | 5.0E-04 | 1.4E-01 | 3.4E-05 | 3.9E-05 | 5.7E-05 | 5.9E-04 |
|  | 8% | 7% | 9% | 0% | 0% | 0% | 0% | 0% | 10% | 10% | 3% | 6% |
| Manufacturing | 2.3E-05 | 9.4E-01 | 9.4E-02 | 4.7E-04 | 2.0E-04 | 1.4E-01 | 5.0E-04 | 1.4E-01 | 3.4E-05 | 3.6E-05 | 4.2E-05 | 5.1E-04 |
|  | 8% | 6% | 8% | 0% | 0% | 0% | 0% | 0% | 10% | 9% | 2% | 5% |
| Transports | 3.8E-11 | 2.0E-01 | 1.4E-02 | 1.3E-04 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 3.7E-06 | 1.4E-05 | 7.7E-05 |
|  | 0% | 1% | 1% | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 1% | 1% |
| Energy losses | 4.7E-06 | 2.2E+00 | 1.8E-01 | 1.1E-03 | 4.0E-05 | 2.0E-02 | 1.0E-04 | 2.0E-02 | 1.3E-04 | 1.2E-05 | 5.7E-05 | 5.6E-04 |
|  | 2% | 14% | 16% | 0% | 0% | 0% | 0% | 0% | 36% | 3% | 3% | 5% |

Table S-30: Overall LCIA results for the baseline scenario. HVDC configuration.

| HVDC |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| according to CML2002 | ADm | ADf | CC | HT | FAET | MAET | FSET | MSET | TET | POF | EUT | ACD |
|  | kg.eq Sb | MJ | kg.eq CO2 | 0 | kg.eq 1,4-DCB/y | kg.eq 1,4-DCB/y | kg.eq 1,4-DCB/y | kg.eq 1,4-DCB/y | kg.eq 1,4-DCB/y | kg.eq etilene/y | kg.eq PO4--/y | kg.eq SO2/y |
| Whole system | 3.1E-04 | 1.9E+01 | 1.6E+00 | 2.3E-01 | 1.0E+00 | 5.4E+02 | 2.4E+00 | 4.7E+02 | 4.6E-04 | 5.9E-04 | 2.0E-03 | 1.2E-02 |
|  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% |
| Cables | 2.6E-04 | 8.8E+00 | 5.9E-01 | 2.2E-01 | 1.0E+00 | 5.4E+02 | 2.4E+00 | 4.7E+02 | 1.9E-04 | 2.5E-04 | 1.4E-03 | 7.8E-03 |
|  | 84% | 46% | 36% | 98% | 100% | 100% | 100% | 100% | 41% | 43% | 70% | 64% |
| Production | 2.6E-04 | 8.4E+00 | 5.6E-01 | 2.2E-01 | 1.0E+00 | 5.4E+02 | 2.4E+00 | 4.7E+02 | 1.9E-04 | 2.3E-04 | 1.3E-03 | 7.2E-03 |
|  | 84% | 44% | 34% | 97% | 100% | 100% | 100% | 100% | 41% | 39% | 66% | 59% |
| Transports | 6.5E-11 | 3.5E-01 | 3.1E-02 | 7.9E-04 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 2.1E-05 | 8.4E-05 | 5.2E-04 |
|  | 0% | 2% | 2% | 0% | 0% | 0% | 0% | 0% | 0% | 4% | 4% | 4% |
| Offshore substation | 2.3E-05 | 6.4E+00 | 6.9E-01 | 3.4E-03 | 2.1E-04 | 1.4E-01 | 5.3E-04 | 1.4E-01 | 7.5E-05 | 2.8E-04 | 4.7E-04 | 3.1E-03 |
|  | 7% | 33% | 43% | 1% | 0% | 0% | 0% | 0% | 16% | 49% | 23% | 26% |
| Manufacturing | 2.3E-05 | 5.8E+00 | 6.3E-01 | 1.8E-03 | 2.1E-04 | 1.4E-01 | 5.3E-04 | 1.4E-01 | 7.5E-05 | 2.4E-04 | 3.0E-04 | 2.1E-03 |
|  | 7% | 30% | 39% | 1% | 0% | 0% | 0% | 0% | 16% | 41% | 15% | 17% |
| Transports | 1.2E-10 | 6.4E-01 | 5.8E-02 | 1.6E-03 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 4.2E-05 | 1.7E-04 | 1.1E-03 |
|  | 0% | 3% | 4% | 1% | 0% | 0% | 0% | 0% | 0% | 7% | 8% | 9% |
| Onshore substation | 2.1E-05 | 1.0E+00 | 9.7E-02 | 5.4E-04 | 1.8E-04 | 1.3E-01 | 4.6E-04 | 1.2E-01 | 3.2E-05 | 3.5E-05 | 5.0E-05 | 5.3E-04 |
|  | 7% | 5% | 6% | 0% | 0% | 0% | 0% | 0% | 7% | 6% | 2% | 4% |
| Manufacturing | 2.1E-05 | 8.5E-01 | 8.5E-02 | 4.3E-04 | 1.8E-04 | 1.3E-01 | 4.6E-04 | 1.2E-01 | 3.2E-05 | 3.2E-05 | 3.8E-05 | 4.7E-04 |
|  | 7% | 4% | 5% | 0% | 0% | 0% | 0% | 0% | 7% | 6% | 2% | 4% |
| Transports | 3.1E-11 | 1.6E-01 | 1.2E-02 | 1.1E-04 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 0.0E+00 | 3.0E-06 | 1.2E-05 | 6.2E-05 |
|  | 0% | 1% | 1% | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 1% | 1% |
| Energy losses | 6.3E-06 | 3.0E+00 | 2.4E-01 | 1.5E-03 | 5.3E-05 | 2.7E-02 | 1.4E-04 | 2.7E-02 | 1.7E-04 | 1.6E-05 | 7.6E-05 | 7.6E-04 |
|  | 2% | 15% | 15% | 1% | 0% | 0% | 0% | 0% | 36% | 3% | 4% | 6% |

# SM7. Supplementary results: sensitivity analysis

Table S-31:Sensitivity analysis results.

|  |  |  | ADm | ADf | CC | HT | POF | EUT | ACD |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| + 20% input | AC | Capacity factor | -19.6% | -16.76% | -16.31% | -19.88% | -19.31% | -19.28% | -18.72% |
|  |  | Lifetime | -19.6% | -16.02% | -15.36% | -19.73% | -17.09% | -17.33% | -16.59% |
|  |  | Onshore substation | 0.7% | 2.02% | 2.98% | 0.05% | 3.20% | 0.88% | 1.18% |
|  |  | Jacket | 0.0% | 1.78% | 2.70% | 0.03% | 2.89% | 0.81% | 0.89% |
|  |  | Offshore substation | 1.6% | 1.40% | 1.84% | 0.05% | 1.88% | 0.59% | 1.10% |
|  |  | T2 | 0.0% | 0.27% | 0.27% | 0.01% | 0.20% | 0.17% | 0.16% |
|  |  | T1 | 0.0% | 0.15% | 0.15% | 0.01% | 0.11% | 0.09% | 0.09% |
|  | DC | Capacity factor | -19.5% | -16.42% | -16.50% | -19.84% | -19.36% | -19.11% | -18.53% |
|  |  | Lifetime | -19.5% | -15.81% | -15.82% | -19.68% | -17.80% | -17.28% | -16.67% |
|  |  | Offshore substation | 1.5% | 3.58% | 4.52% | 0.11% | 4.75% | 1.78% | 2.19% |
|  |  | Jacket | 0.0% | 2.37% | 3.09% | 0.06% | 3.23% | 1.22% | 1.24% |
|  |  | Onshore substation | 1.3% | 1.05% | 1.19% | 0.05% | 1.19% | 0.49% | 0.86% |
|  |  | T2 | 0.0% | 0.25% | 0.21% | 0.01% | 0.15% | 0.17% | 0.15% |
|  |  | T1 | 0.0% | 0.13% | 0.11% | 0.01% | 0.08% | 0.09% | 0.08% |
| - 20% input | AC | Capacity f. | 19.7% | 17.71% | 17.38% | 19.92% | 19.53% | 19.52% | 19.13% |
|  |  | Lifetime | 19.7% | 17.16% | 16.65% | 19.82% | 17.96% | 18.14% | 17.59% |
|  |  | Onshore | -0.7% | -2.10% | -3.16% | -0.05% | -3.42% | -0.90% | -1.21% |
|  |  | Jacket | 0.0% | -1.84% | -2.85% | -0.03% | -3.06% | -0.82% | -0.90% |
|  |  | Offshore | -1.6% | -1.44% | -1.91% | -0.05% | -1.95% | -0.60% | -1.13% |
|  |  | T2 | 0.0% | -0.28% | -0.27% | -0.01% | -0.20% | -0.17% | -0.16% |
|  |  | T1 | 0.0% | -0.15% | -0.15% | -0.01% | -0.11% | -0.09% | -0.09% |
|  | DC | Capacity f. | 19.7% | 17.46% | 17.52% | 19.89% | 19.57% | 19.40% | 18.99% |
|  |  | Lifetime | 19.7% | 17.00% | 17.00% | 19.79% | 18.47% | 18.10% | 17.65% |
|  |  | Offshore | -1.5% | -3.85% | -4.96% | -0.11% | -5.25% | -1.85% | -2.29% |
|  |  | Jacket | 0.0% | -2.49% | -3.29% | -0.06% | -3.46% | -1.25% | -1.27% |
|  |  | Onshore | -1.4% | -1.07% | -1.21% | -0.05% | -1.22% | -0.50% | -0.87% |
|  |  | T2 | 0.0% | -0.25% | -0.21% | -0.01% | -0.15% | -0.17% | -0.15% |
|  |  | T1 | 0.0% | -0.14% | -0.11% | -0.01% | -0.08% | -0.09% | -0.08% |

# SM8. Supplementary results: scenario analysis

Table S-32: selection of the type and number of cables for each scenario.

| Power | Distance | AC/DC | Cable type | N° of cables |
| --- | --- | --- | --- | --- |
| 200 | 25 | AC | kV220Tmm500 | 1 |
| 200 | 25 | DC | kV150mm500 | 1 |
| 200 | 50 | AC | kV220Tmm500 | 1 |
| 200 | 50 | DC | kV150mm500 | 1 |
| 200 | 100 | AC | kV220Tmm500 | 1 |
| 200 | 100 | DC | kV150mm500 | 1 |
| 200 | 150 | AC | kV220Tmm800 | 1 |
| 200 | 150 | DC | kV150mm500 | 1 |
| 200 | 200 | AC | kV132mm500 | 2 |
| 200 | 200 | DC | kV150mm500 | 1 |
| 200 | 250 | AC | kV220Smm1600 | 1 |
| 200 | 250 | DC | kV150mm500 | 1 |
| 500 | 25 | AC | kV220Tmm500 | 2 |
| 500 | 25 | DC | kV320mm630 | 1 |
| 500 | 50 | AC | kV220Tmm500 | 2 |
| 500 | 50 | DC | kV320mm630 | 1 |
| 500 | 100 | AC | kV220Tmm630 | 2 |
| 500 | 100 | DC | kV320mm630 | 1 |
| 500 | 150 | AC | kV220Smm1400 | 1 |
| 500 | 150 | DC | kV320mm630 | 1 |
| 500 | 200 | AC | kV220Smm1600 | 1 |
| 500 | 200 | DC | kV320mm630 | 1 |
| 500 | 250 | AC | kV220Smm1600 | 2 |
| 500 | 250 | DC | kV320mm630 | 1 |
| 1000 | 25 | AC | kV400mm1400 | 1 |
| 1000 | 25 | DC | kV320mm1400 | 1 |
| 1000 | 50 | AC | kV400mm1600 | 1 |
| 1000 | 50 | DC | kV320mm1400 | 1 |
| 1000 | 100 | AC | kV400mm1600 | 1 |
| 1000 | 100 | DC | kV320mm1400 | 1 |
| 1000 | 150 | AC | kV400mm1400 | 2 |
| 1000 | 150 | DC | kV320mm1400 | 1 |
| 1000 | 200 | AC | kV220Smm1600 | 2 |
| 1000 | 200 | DC | kV320mm1400 | 1 |
| 1000 | 250 | AC | not feasible | - |
| 1000 | 250 | DC | kV320mm1400 | 1 |

Figure S-6: Results of the scenario analysis for selected LCIA indicators.

# SM9. Supplementary results: scenario analysis - recycling

Figure S-7: Climate change indicator calculated for HVAC and HVDC transmission systems as a function of distance to shore and power rating. Panel a): without dismantling and recycling phases; panel b): with dismantling and recycling phases.

# SM10. Inventory data for the background EoL processes

Table S-33: Datasets used in LCI modelling for the EoL processes. The recycle processes and waste treatment processes for steel and stainless steel are assumed to be the same.

| Process | Corresponding dataset adopted in LCI modelling | Source | Year | Location | Link |
| --- | --- | --- | --- | --- | --- |
| Copper recycle | Recycling of copper from clean scrap; collection, transport, pretreatment; production mix, at plant; copper content in input scrap 90%, copper losses 1% | Thinkstep - Free Gabi data | 2015 | EU+ EFTA+ UK | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=0e206ca6-5ee9-4e65-b8f4-fc70c923e7b5&version=20.06.000&stock=EF_20_official_data |
| Steel recycle | Recycling of steel into steel billet; collection, transport, pretreatment, remelting; production mix, at plant; steel waste, efficiency 95% | Thinkstep - Free Gabi data | 2015 | EU+ EFTA+ UK | https://lcdn.thinkstep.com/datasetdetail/process.xhtml?uuid=7bd54804-bcc4-4093-94e4-38e4facd4900&version=20.06.000&stock=EF_20_official_data |
| Stainless steel recycle | Recycling of steel into steel billet; collection, transport, pretreatment, remelting; production mix, at plant; steel waste, efficiency 95% | Thinkstep - Free Gabi data | 2015 | EU+ EFTA+ UK | https://lcdn.thinkstep.com/datasetdetail/process.xhtml?uuid=7bd54804-bcc4-4093-94e4-38e4facd4900&version=20.06.000&stock=EF_20_official_data |
| HDPE recycle | High density polyethylene (HDPE), recycled; washing, drying, shredding, pelletizing; production mix, at plant; Erec/ErecEoL, efficiency 98% | Ecoinvent - EF3_1_Plastic_public | 2016 | GLO | https://ecoinvent.lca-data.com/datasetdetail/process.xhtml?uuid=42a68157-3aa4-5d42-bd85-cc46bea9b85f&version=01.01.000&stock=default |
| XLPE recycle | High density polyethylene (HDPE), recycled; washing, drying, shredding, pelletizing; production mix, at plant; Erec/ErecEoL, efficiency 98% | Ecoinvent - EF3_1_Plastic_public | 2016 | GLO | https://ecoinvent.lca-data.com/datasetdetail/process.xhtml?uuid=42a68157-3aa4-5d42-bd85-cc46bea9b85f&version=01.01.000&stock=default |
| PP recycle | Polypropylene, recycled, post-consumer; washing, drying, shredding, pelletizing; production mix, at plant; Erec/ErecEoL, efficiency 90% | Ecoinvent - EF3_1_Plastic_public | 2016 | GLO | https://ecoinvent.lca-data.com/datasetdetail/process.xhtml?uuid=6e84c83b-bd4e-5e5a-a002-47c31ade57e6&version=01.01.000&stock=EF3_1_Plastics_public |
| Lead recycle | Secondary lead; secondary production, melting of lead scrap; single route, at plant; 11.3 g/cm3 | Thinkstep -Free Gabi data | 2012 | EU-28 +EFTA | https://lcdn.thinkstep.com/datasetdetail/process.xhtml?uuid=175f9462-6733-4dbb-a939-75525d3f70b3&version=18.07.025&stock=EF_20_official_data |
| Waste HDPE | market for waste polyethylene | Ecoinvent - V3.9.1 (2022) | 2018 | DE | https://ecoquery.ecoinvent.org/3.9.1/cutoff/dataset/18545/impact_assessment |
| Waste PP | market for waste polypropylene | Ecoinvent - V3.9.1 (2022) | 2018 | DE | https://ecoquery.ecoinvent.org/3.9.1/cutoff/dataset/19152/documentation |
| Waste Steel | market for scrap steel | Ecoinvent - V3.9.1 (2022) | 2018 | DE | https://ecoquery.ecoinvent.org/3.9.1/cutoff/dataset/15758/documentation |
| Waste Stainless Steel | market for scrap steel | Ecoinvent - V3.9.1 (2022) | 2018 | DE | https://ecoquery.ecoinvent.org/3.9.1/cutoff/dataset/15758/documentation |
| Waste Copper | market for scrap copper | Ecoinvent - V3.9.1 (2022) | 2018 | DE | https://ecoquery.ecoinvent.org/3.9.1/cutoff/dataset/15111/export |
| Waste Lead | Landfill of inert (lead); landfill including leachate treatment and with transport without collection and pre-treatment; production mix (region specific sites), at landfill site | Thinkstep -Free Gabi data | 2015 | EU+ EFTA+ UK | https://lcdn.thinkstep.com/showProcess.xhtml?uuid=7107e3f4-4ebd-4f8d-9e36-ec5d0df9cc3b&version=20.06.000&stock=EF_20_official_data |

# References

[1]	HSM Offshore Energy, “A18 Satellite Platform Project - HSM Offshore Energy.” Accessed: Jun. 06, 2024. [Online]. Available: https://hsmoffshoreenergy.com/project/a18-satellite-platform/

[2]	HSM Offshore Energy, “Blythe Platform Project - HSM Offshore Energy.” Accessed: Jun. 06, 2024. [Online]. Available: https://hsmoffshoreenergy.com/project/blythe-platform-project/

[3]	HSM Offshore Energy, “Southwark Platform Project - HSM Offshore Energy.” Accessed: Jun. 06, 2024. [Online]. Available: https://hsmoffshoreenergy.com/project/southwark-platform-project/

[4]	GCaptain, “Kvaerner Wins NOK 1.2 Billion Contract for Hild Jacket Delivery Offshore Norway.” Accessed: Jun. 06, 2024. [Online]. Available: https://gcaptain.com/kvaerner-wins-billion-contract/

[5]	Nordsee One, “Offshore substation of the Nordsee One wind park.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.nordseeone.com/engineering-construction/offshore-substation.html

[6]	NS Energy Business, “Race Bank Offshore Wind Farm in North Sea, the UK.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.nsenergybusiness.com/projects/race-bank-offshore-wind-farm-north-sea-uk/

[7]	Renewable Technology, “Gwynt y Môr Offshore Wind Project, Liverpool Bay, North Wales - Renewable Technology.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.renewable-technology.com/projects/gwynt-y-mr-offshore-wind-project-liverpool-bay-north-wales/

[8]	ISC, “Gode Wind 1 - ISC Consulting Engineers A/S.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.isc.dk/en/projects/gode-wind-i

[9]	TECON WASIT, “WORK DESCRIPTION v1,” p. 1, 2013.

[10]	Offshore Wind, “Arkona Offshore Substation Stands Tall | Offshore Wind.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.offshorewind.biz/2018/04/09/arkona-offshore-substation-stands-tall/

[11]	Offshore Wind, “Jan De Nul Loads First Taiwan-Bound Jackets in South Korea | Offshore Wind.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.offshorewind.biz/2020/05/21/jan-de-nul-loads-first-taiwan-bound-jackets-in-south-korea/

[12]	Offshore Energy, “McDermott installs platform with largest jacket in Vietnam - Offshore Energy.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.offshore-energy.biz/mcdermott-installs-platform-with-largest-jacket-in-vietnam/

[13]	T. Nasseri, N. Shabakhty, and M. Hadi Afshar, “Study of Fixed Jacket Offshore Platform in the Optimization Design Process under Environmental Loads,” International Journal of Maritime Technology Ijmt, vol. 2, no. January 2015, pp. 75–84, 2014.

[14]	Upstream, “COOEC rolls out Asia’s largest offshore jacket | Upstream.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.upstreamonline.com/field-development/cooec-rolls-out-asia-s-largest-offshore-jacket/2-1-1188703

[15]	EnergyVoice, “In Pictures: Aberdeen Offshore Wind Farm jackets wait in Peterhead Port - News for the Energy Sector.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.energyvoice.com/renewables-energy-transition/166916/in-pictures-aberdeen-offshore-wind-farm-jackets-wait-in-peterhead-port/

[16]	Cometto, “Final destination of a 3,700 tons offshore jacket - Self-propelled vehicles.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.cometto.com/stories/final-destination-3700-tons-offshore-jacket-spmt/

[17]	Global Times, “Asia’s deepest deep-water offshore jacket platform ‘Haiji No.1’ begins operations - Global Times.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.globaltimes.cn/page/202210/1276535.shtml

[18]	Heerema, “HelWin l Heerema.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.heerema.com/heerema-marine-contractors/offshore-wind/helwin

[19]	IV company, “DolWin Alpha HVDC offshore platform - Iv-Groep.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.iv.nl/en/projects/dolwin-alpha-hvdc-offshore-platform/

[20]	General Electric, “DolWin3HVDC Voltage Source Converters  for Efficient Connection of Renewable Energy,” 2018.

[21]	SINTEF energy research, “Technology perspectives of the North Sea Offshore and storage Network (NSON),” 2015.

[22]	T. Daten, “Fact Sheet BorWin3 Netzanbindungssystem,” no. Dc, 2020.

[23]	Dragados Offshore, “BorWin5 HVDC CONVERTER PLATFORM,” no. May, p. 2025, 2025.

[24]	Renewable Energy News, “borwin-gamma-wears-jacket - reNews - Renewable Energy News.” Accessed: Jun. 06, 2024. [Online]. Available: https://renews.biz/31679/borwin-gamma-wears-jacket/

[25]	TENNET; Siemens energy; Dragados Offshore, “DolWin kappa,” no. April, pp. 8–11, 2022.

[26]	Semco Maritime, “Hornsea Project One offshore substation.” Accessed: Jun. 06, 2024. [Online]. Available: https://www.semcomaritime.com/cases/hornsea-project-one

[27]	Orsted, “Orsted.co.uk.” Accessed: Jun. 21, 2024. [Online]. Available: https://orsted.co.uk/

[28]	Nordsee One, “Nordsee One - Offshore Wind Farm in the North Sea.” Accessed: Jun. 21, 2024. [Online]. Available: https://www.nordseeone.com/

[29]	E.ON Climate & Renewables Services, “Offshore Wind Farm Arkona,” https://studio-szczesny.de/_media/E.ON-ofshore.pdf, 2014.

[30]	HSM Offshore Energy, “HORNS REV C OHVS Project - 400 MW - HSM Offshore Energy.” Accessed: Jun. 06, 2024. [Online]. Available: https://hsmoffshoreenergy.com/project/horns-rev-c-offshore-high-voltage-substation-400-mw/

[31]	Offshore Wind Programme Board, “Lightweight Offshore Substation Designs Final Summary Report January 2016,” no. January, 2016.

[32]	Tractebel Overdick, “MOAB® HELWIN alpha | Overdick — Offshore Engineering, Naval Architecture — Hamburg, Kuala Lumpur.” Accessed: Jun. 06, 2024. [Online]. Available: https://overdick-offshore.com/projects/offshore-wind/helwin_alpha

[33]	Tractebel Overdick, “MOAB® BORWIN beta | Overdick — Offshore Engineering, Naval Architecture — Hamburg, Kuala Lumpur.” Accessed: Jun. 06, 2024. [Online]. Available: https://overdick-offshore.com/projects/offshore-wind/borwin_beta

[34]	Tractebel Overdick, “HVDC SYLWIN alpha | Overdick — Offshore Engineering, Naval Architecture — Hamburg, Kuala Lumpur.” Accessed: Jun. 06, 2024. [Online]. Available: https://overdick-offshore.com/projects/offshore-wind/hvdc_sylwin_alpha

[35]	RWE, “Construction – Triton Knoll Onshore Substation – Triton Knoll.” Accessed: Jun. 17, 2024. [Online]. Available: https://www.tritonknoll.co.uk/onshore-sub/

[36]	Siemens, “First Moray East onshore transformer arrives on site.” Accessed: Jun. 17, 2024. [Online]. Available: https://news.siemens.co.uk/news/first-moray-east-onshore-transformer-arrives-on-site

[37]	“Necton Onshore Substation - Google Maps.” Accessed: Jun. 17, 2024. [Online]. Available: https://www.google.com/maps/place/Necton+Onshore+Substation/@52.6606133,0.7932376,217m/data=!3m1!1e3!4m6!3m5!1s0x47d9d52b09339407:0x71ef74309f586f5f!8m2!3d52.6605557!4d0.7935858!16s%2Fg%2F11c1mzp8qf?entry=ttu

[38]	“Beatrice Onshore Substation - Offshore Windfarm - Google Maps.” Accessed: Jun. 17, 2024. [Online]. Available: https://www.google.com/maps/place/Beatrice+Onshore+Substation+-+Offshore+Windfarm/@57.5236729,-2.956263,384m/data=!3m1!1e3!4m6!3m5!1s0x4885aba2f9105c65:0x5fe47ba90ce64b1f!8m2!3d57.5234822!4d-2.95378!16s%2Fg%2F11g153wvbh?entry=ttu

[39]	D. Retzmann, “HVDC Station Layout, Equipment LCC & VSC and Integration of Renewables using HVDC,” Cigre Tutorial, 2012, [Online]. Available: http://www.ptd.siemens.de/Cigre_AUS_2011_HVDC_&_GridAccess_tutorial_Re.pdf

[40]	Beijing Power Equipment Group, “Dry type air core reactors,” no. 12, 2003, [Online]. Available: http://bpeg-usa.com/resources/BPEG_Reactors.pdf

[41]	“Cost planning - Industrial buildings - SteelConstruction.info.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.steelconstruction.info/Cost_planning_-_Industrial_buildings

[42]	“COBRA Eemshaven - Google Maps.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.google.com/maps/place/COBRA+Eemshaven/@53.4355206,6.866604,213m/data=!3m1!1e3!4m6!3m5!1s0x47b6275cb72b15dd:0x1c520c09888a2048!8m2!3d53.4353196!4d6.8674199!16s%2Fg%2F11fzj9n00v?hl=en&entry=ttu

[43]	“Station Endrup (EDR) - Energinet.dk - Google Maps.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.google.com/maps/place/Station+Endrup+(EDR)+-+Energinet.dk/@55.5301277,8.7026231,202m/data=!3m1!1e3!4m15!1m8!3m7!1s0x464b3d9ce7b72809:0xa00afcc1d50a370!2s6740+Endrup,+Denmark!3b1!8m2!3d55.523115!4d8.718392!16s%2Fg%2F121_p8cf!3m5!1s0x464b3d6e836eff21:0xd4259819b75320f5!8m2!3d55.531789!4d8.7056998!16s%2Fg%2F11jts01h62?hl=en&entry=ttu

[44]	“Umspannwerk Dörpen West - Google Maps.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.google.com/maps/place/Umspannwerk+D%C3%B6rpen+West/@52.9820068,7.2525101,430m/data=!3m1!1e3!4m6!3m5!1s0x47b7b9378840bf3b:0x7f233d698ed8b47a!8m2!3d52.9819893!4d7.2527402!16s%2Fg%2F11fj1pz212?authuser=0&entry=ttu

[45]	“VSC HVDC Transformers Installed on DolWin3 Offshore Converter Platform | LinkedIn.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.linkedin.com/pulse/vsc-hvdc-transformers-installed-dolwin3-offshore-converter-neil-kirby/

[46]	“Blackhillock Substation - Google Maps.” Accessed: Jun. 18, 2024. [Online]. Available: https://www.google.com/maps/place/Blackhillock+Substation/@57.5228459,-2.9507943,516m/data=!3m1!1e3!4m6!3m5!1s0x4885ab8129970a05:0x1b6301263a08e0e5!8m2!3d57.5222549!4d-2.9449712!16s%2Fg%2F11h31z9mp9?authuser=0&entry=ttu

[47]	ABB, “XLPE Submarine Cable Systems,” p. 12, 2014.

[48]	Prysmian, “High Voltage Cables,” 2007.

[49]	ZTT group, “Submarine Cable,” 2000.

[50]	C. H. Chien and R. W. G. Bucknall, “Analysis of harmonics in subsea power transmission cables used in VSC-HVDC transmission systems operating under steady-state conditions,” IEEE Transactions on Power Delivery, vol. 22, no. 4, pp. 2489–2497, 2007, doi: 10.1109/TPWRD.2007.905277.

[51]	ABB, “Submarine Cable Design Sheet – 1,000 MW DC,” no. 135 mm, p. 20100695, 2011.

[52]	A. I. Tariq and A. M. Saleh, “An experimental investigation into the combustion properties, performance, emissions, and cost reduction of using heavy and light fuel oils,” Case Studies in Thermal Engineering, vol. 44, no. December 2022, p. 102832, 2023, doi: 10.1016/j.csite.2023.102832.

[53]	Prysmian powerlink, “Giulio Verne cable laying ship specification,” 2004.

[54]	C. Birkeland, “Assessing the Life Cycle Environmental Impacts of Offshore Wind Power Generation and Power Transmission in the North Sea,” 2011.

[55]	A. Arvesen, C. Birkeland, and E. G. Hertwich, “The importance of ships and spare parts in LCAs of offshore wind power,” Environ Sci Technol, vol. 47, no. 6, pp. 2948–2956, 2013, doi: 10.1021/es304509r.

[56]	J. S. Finn, J. MacEnri, and R. Szewczyk, “Guidelines for the design and construction of AC offshore substations for wind power plants,” CIGRE Working Group, vol. B3-26, no. December, p. 378, 2011.

[57]	Fred.Olsen Wincarrier, “Jack-Up Installation Vessel Blue Tern,” pp. 2–3, 2013.